# Building Management Systems (BMS) – Seminar 2 – Advanced Management and Improvement Opportunities
Presented By: Andrew Smith, Leader Building Technologies – A.G. Coombs Advisory

Contents

Seminar 2 – Advanced Management and Improvement Opportunities	3

BMS Types and Scalability	3

Open System Protocols – What does this mean?	3

Open System Protocols – Comparison	3

High Level Interfaces (HLIs)	4

Integration with other building systems	4

Distributed Building Control Networks	4

Licensing and Other Limitations	5

BMCS Programming	5

Application Programming – Control Loops	5

Standard Programming Loops – P, PI, PID	5

Advanced Programming for Energy Efficiency	6

Control Loop Tuning – Recap	7

Extended BMCS Functionality	7

Advanced User Interface Functions	7

Trend Data and Trend Logging	7

Automated Reporting	8

Alarms and Alarm Management	8

Upgrades and Retrofits	8

When to Upgrade or Retrofit	8

Partial or Staged Upgrade Options	9

Total System Replacement	9

Opportunity to Set New Standards	9

Decommissioning and Commissioning	10

Advanced Management and Improvement Opportunities – Recap	10

## Seminar 2 – Advanced Management and Improvement Opportunities

- BMCS System Architecture

- BMCS Programming

- Extended BMCS Functionality

- Upgrades and Retrofits

Seminar 1 – The Basics Explained

- What is a BMCS?

- What Does it Do?

- Benefits

- Operational Considerations

## BMS Types and Scalability

- Can be a single BMS controller to hundreds of networked controllers

- Have a basic LCD display, a simple WEB interface through to fully animated Graphic Operator Workstations.

- Basic pre-programmed (canned) control functions to fully customised  and freely programmable

- Stand-alone BMS or fully integrated into other building systems

## Open System Protocols – What does this mean?

- The term ‘Open System’ is often confused with ‘Open Protocols’ but these terms are not interchangeable.

- An ‘Open Protocol’ refers to an industry standard communications dialog that allows BMS controllers to communicate together much like PCs talk on a network in a common language. Two of the major protocols in use are;

- Do not be confused by which one is the better alternative or which one provides vender independence. Vendor specific configuration tools are still required

- What you need is an ‘Open System’ and this has less to do with technology and more to do with venders attitude, its staff and their engineering expertise.

## Open System Protocols – Comparison

- Each device can be from a different manufacturer

- Use each individual manufacturers user interface to configure and  program their equipment only

- Connections made between the devices with standard connections

- Data is shared between the devices via standard industry protocols

- Standard protocol ensures interoperability between devices

- Each device can be replaced with one from a different manufacturer

## High Level Interfaces (HLIs)

- Communication between devices or complete systems over a data network

- Enable integration between building systems

- Replaces traditional ‘hard wired’ connections between devices

- Can provide data for hundreds of points over a single connection

- Provides additional information and extended functionality

- Communications can be custom interfaces or standard open protocols

- Open system protocols include Lonworks, Bacnet or Modbus.

- Standard Open protocols reduce configuration, engineering, etc

## Integration with other building systems

- There are many reasons to integrate the BMS with other building systems…

  - Single user interface to monitor and control all building services

  - Consolidated Alarm and Fault management

  - Extended Functionality such as:

    - Single point for all time scheduling functions

    - Electrical load management based on energy system

    - Consolidated after hours control of lighting and HVAC

    - Occupancy control of HVAC using Security and Access Control

    - Lighting control in the event of a security breach

    - Extended secondary fire mode control of lighting, security, etc*

*All primary fire mode controls must meet Australian standards

## Distributed Building Control Networks

- Building control functions don’t have to be limited to being performed within the BMS controllers alone

- Networks, High Level Interfaces (HLI) and integration allow control functionality to be distributed

- Devices include Variable Speed Drives (VSDs), chillers and packaged and split air conditioning units

- Each device directly performs its own specialised control

- Via the HLI, the BMS monitors operational status and allows for adjustment of control parameters such time schedules and setpoints

## Licensing and Other Limitations

- When selecting a BMS consideration should be made with regard to all relevant software and point licensing, network limitations and spare capacity

  - Licenses associated to the number of points connected to the BMS

  - Licenses of configuration tools used to configure the BMS

  - Data network limitations to the number of connected BMS controllers

  - System design should allow for spare capacity for future expansion

  - WEB user interfaces may have license restrictions for connected PCs

  - Maintenance issues if your BMS is not current software revisions?

## BMCS Programming

- Application programming

  - Canned, graphical, event and script

- Standard programming loops such as PID, PI and P

- Advanced programming strategies for energy efficiency

- Control loop tuning and energy optimisation

### Application Programming – Control Loops

- There are 2 basic types of control Loops, event driven and closed loop.

- Event driven control which triggers from a change of state event such as time schedules or the change of state of an input (analog or digital)

- Closed loop control continually uses the controlled variable as feed-back and adjusts the output device in direct response.

### Standard Programming Loops – P, PI, PID

- The most commonly referenced control loop – the PID loop

‘P’ = Proportion control band

‘I’ = Integral gain control

‘D’ = Derivative term

- Can be either P only, P+I or PID (rare)

- Each loop needs an input variable, a setpoint, an output control variable and a loop timer

- Proportional Band – a value based on the error from setpoint

- Integral Gain – added value based on how long the error has existed

- Derivative Term – added value based on the speed the input variable is changing

- Dead Band – a range close to the setpoint when no change occurs

- Loop Timer – How often to check the input variable against setpoint

- P Only – Loop settles with an error from setpoint

- P+I – Control variable close to setpoint, output maintained

- PID – Same as P+I but faster to respond, output maintained

### Advanced Programming for Energy Efficiency

- Control algorithms focused on energy efficiency

- Allow for a wider range of acceptable conditions

- Aim to use just enough heating or cooling

- Start up just in time and run just for long enough

- Remove all overlap between systems

- Sequences that match plant capacity to building load

- Use most energy efficient plant when possible

- Automatically adjust for seasonal conditions

- Part load, building turn down or part occupancy

Energy Efficiency Control Strategies

- Examples of energy efficient control strategies include:

  - Optimal start up – Start the air conditioning at the latest possible time to reach comfort conditions as the building becomes occupied

  - Optimal plant stop – Stop the heating and cooling plant at the earliest possible time to allow the system inertia to maintain conditions

  - Proportional only zone control – Allow a wider range of acceptable temperature but within limits

  - Variable air pressure control – Automatically adjust the fan speed control  to provide just enough air

  - Variable water pressure control – Automatically adjust the pump speed control to provide just enough water

  - Variable cooling water temperature – only chill the cooling water enough to cater for the building load

### Control Loop Tuning – Recap

- BMS control  loop Tuning and Optimisation are not the same thing

- BMS control loop tuning ensures that the equipment operates in a stable, predictable and repeatable manner.

- Optimisation focuses on operating the equipment in the most energy efficient manner without impacting on the tenant comfort

- The first stage of optimisation includes BMS loop tuning.

## Extended BMCS Functionality

- Advanced User interface functions

- Trend data, sampling rates and numbers of samples

- Automated reporting

- Alarm and event management

### Advanced User Interface Functions

- Operator override control and adjustment of BMS points

- Condition based alarming and alarm management options

- Point trend sampling trend logging, graphing and data export

- Automated and customised reporting

- Multiple user access levels, view only to administrator

- Operator activity logging and audit trails

- Real time monitoring of control logic

### Trend Data and Trend Logging

- BMS trending provides a historical look at plant performance

- Allows a retrospective look at control for fault finding and fine tuning

- Trend sampling is set up for individual BMS points

- Analogue BMS points are usually sampled at intervals

- Binary BMS points are usually sampled on a change of state (COV)

- The interval between samples should reflect the rate the point changes

- Incorrect sampling rates will distort results or mask problems

- Individual point trends can be grouped and displayed logically

- Group point trends to put performance into context

- Keep enough trend data history to allow for full analysis

### Automated Reporting

- Reports set up to run automatically based on time or event

- Can also apply to automatically grouping predefined points

- Can be system related such as operator override or alarms

- Can also be customised for the installation

- Operational summaries of critical plant or groups of items

- Related to maintenance events such as fire mode testing

- Multiple output options including printer, exports and email

### Alarms and Alarm Management

- BMS Points can have multiple alarm states

- Alarms can be conditional, suppressed or delayed

- Multiple alarm levels, notification, warning, critical, fire life safety

- Selectable alarm actions, acknowledged, repeated

- Alarm output options include Screen, Printer, SMS and email

- Alarm summaries include active alarms and historical alarm logs

## Upgrades and Retrofits

- When to retrofit or upgrade

- Partial or staged upgrade options

- Total system replacement

- The opportunity to set new standards

- Importance of decommissioning and commissioning

### When to Upgrade or Retrofit

- When should you consider to upgrade or retrofit?

  - Availability of BMS hardware spare parts or technical support

  - Reliability issues with the current BMS

  - Access to functionality to improve energy efficiency

  - Major building fit out project or plant upgrade

  - Identify the key objectives and drivers

- What are the options, upgrade, migration, full replacement

- What will the impacts be on my building and tenants?

- Plan well in advance, don’t wait until the last minute

- Consider getting some independent advice

### Partial or Staged Upgrade Options

- Update to a newer version of the current BMS

- Allows for refresh of existing system at reduced cost

- Access to new functions and features

- Can target BMS hardware devices at end of life or obsolete

- Opportunity to review control strategies and user interfaces

- Works can be sequenced with tenant churn or retrofits

- Logistically a simpler option than full replacement

### Total System Replacement

- Total replacement of the current BMS hardware and software

- Opportunity to select best available BMS solution for site

- Some field input and output devices can be retained

- New high speed communications network should be included

- Logistical challenges for a tenanted buildings

- A well-developed change over works program is required

- Requires full commissioning of the entire system

### Opportunity to Set New Standards

- Don’t just copy what you already have

- Opportunity to review all control strategies

- Upgrade to energy efficient control

- Set standards for new user interfaces, especially graphic displays

- Take time to workshop and document requirements

- Agree on user interfaces, trending, alarming and reporting

- It’s your system so take an active role

### Decommissioning and Commissioning

- Decommissioning is just as important as commissioning

- Capture years of improvements and ‘enhancements’

- A chance to right the wrongs

- Chance to address the underlying issues

- ‘Point to Point’ testing of all connected field equipment

- Software and hardware commissioning

- Seasonal commissioning and tuning

- Generic calibration factors do not work

- Don’t just commission by faults

## Advanced Management and Improvement Opportunities – Recap

- Building Management Systems are scalable from one to many devices

- Can use standard open protocols to communicate to other systems

- Allow for distributed control functionality with specialised equipment

- Include complex control options to achieve energy efficient operation

- Include functionality to manage and fine tune building performance

- Require good sound planning when implementing or upgrading

- Are not ‘Black Boxes’ and should be utilised to their full potential.